## PM Schedule - ETP (hidden)
CHI |  |  | PREVENTIVE MAINTENANCE SCHEDULE |  | BUSINESS UNIT | CHI
[5 empty] | DEPARTMENT | ENGINEERING
[5 empty] | SECTION | ETP
DOCUMENT NO
ISSUE DATE
NEXT REVISION DATE
AMENDMENT DATE
AMENDMENT NO
[5 empty] | PAGE NO | 1 OF 1
ANNEXURE - 1
SL. NO. | ASSET CODE | *NAME OF MACHINE / EQUIPMENT | MAKE | TYPE | YEAR OF MFG. | CAPACITY | WEEKLY | MONTHLY | ANNUALLY
A |  | ETP
1 |  | EQUALIZATION TANK | N/A | Concrete Material |  |  | * Check tank body and pipes for leakages * Check proper operation of valves * Check proper operation of water level indicators * Clean pump strainers |  | * Annual inspection of tanks (UTM, etc.) * Annual integrity of beams and structure
2 |  | CST TANK 1 | N/A
3 |  | CST TANK 2 | OBITECH | Fibre Material | 2023
4 |  | UASB REACTOR | N/A | Concrete
5 |  | AERATION TANK 1 | OBITECH | Fibre Material | 2023
6 |  | AERATION TANK 2 | N/A
7 |  | ALKALI DOSING TANK | N/A
8 |  | ACID DOSING TANK | N/A
9 |  | BUFFER TANK | N/A
10 |  | SLUDGE SUMP TANK | N/A
11 |  | HOPPER BOTTOM SETTLING TANK | N/A
12 |  | LAMELLA CLARIFIER TANK | N/A
13 |  | HOLDING SUMP TANK | N/A
14 |  | DECANTER CENTRIFUGE TANK | N/A
15 |  | ACTIVATED CARBON FILTER TANK | N/A |  |  |  | * Daily backwashing of filters | * Inspection of isolator & actuator valves, where applicable | * Inspection of filter media and replenish where necessary * Servicing of components (pressure switches, guages, air hose) * Epoxy painting of vessels, if necessary
16 |  | PRESSURE SAND FILTER TANK | N/A
17 |  | SOFTENER PLANT
18 |  | DAF |  |  |  |  | * Inspect scooper shaft for wear and vibration | * Grease pillow bearing | * Replacement of resin beads every 2 years
19 |  | AERATION BLOWER |  |  |  |  | * Cleaning of blower air filter * Inspection of blower parts | * Inspection of oil level | * Replace oil * Replace air filter * Replace oil filter
20 |  | EQUALIZATION TANK PUMPS |  |  |  |  | * Check functionality of isolation valves * Check of leakage of pipes on line | * Cleaning of pump strainers * Check condition of bearings using CBM instrument | * Servicing of transfer pumps
21 |  | CST TANK 1 PUMPS
22 |  | CST TANK 2 PUMPS
23 |  | UASB REACTOR PUMPS
24 |  | AERATION TANK 1 PUMPS
25 |  | AERATION TANK 2 PUMPS
26 |  | BUFFER TANK PUMPS
27 |  | SLUDGE SUMP TANK PUMPS
28 |  | HOPPER BOTTOM SETTLING TANK PUMPS
29 |  | LAMELLA CLARIFIER TANK PUMPS
30 |  | HOLDING SUMP TANK PUMPS
31 |  | DECANTER CENTRIFUGE TANK PUMPS
32 |  | BIOGAS TRANSFER PUMPS
33 |  | FLOWMETERS |  |  |  |  | * Check functionality of flowmeters |  | * Annual calibration of flowmeters
34 |  | PRESSURE GUAGES |  |  |  |  | * Check functionality of pressure gauges |  | * Annual calibration of pressure guages
35 |  | BIO GAS SYSTEM |  |  |  |  | * Physical inspection & lifting of safety relief valves * Check for leakages | * Blowing of gas line filter * Cleaning of foam trap * Cleaning of sediment trap | * Annual overhauling of biogas filter
36 |  | BIO GAS BALLOON |  |  |  |  | * Check for leakages | * Check for wear and tear on ballon strap and anchor
37 |  | BIO GAS GENERATOR
PREPARED BY |  |  | APPROVED BY
Note: N/A - Not Applicable

## UTI PM Log - Daily
| 8 Pages | 52 Copies | [9 empty] | 8 Pages | 52 Copies
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI |  | CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI
[7 empty] | DEPARTMENT |  | ENGINEERING | [8 empty] | DEPARTMENT |  | ENGINEERING
[7 empty] | SECTION |  | UTILITY | [8 empty] | SECTION |  | UTILITY
[7 empty] | DOCUMENT NO |  | CHIENGUTRG08 | [8 empty] | DOCUMENT NO |  | CHIENGUTRG08
[7 empty] | ISSUE DATE | [10 empty] | ISSUE DATE
[7 empty] | PAGE NO |  | 1 OF 1 | [8 empty] | PAGE NO |  | 1 OF 1
Legends | [10 empty] | Legends
Done Ok "√", Not Done "--", Done Not Ok "X" | [10 empty] | Done Ok "√", Not Done "--", Done Not Ok "X"
|  | Date | [10 empty] | Date
S/N | *NAME OF MACHINE / EQUIPMENT | DAILY | Sun (Done / Not Done) | Engr / Operator Sign | Mon (Done / Not Done) | Engr / Operator Sign | Tues (Done / Not Done) | Engr / Operator Sign | Wed (Done / Not Done) | Engr / Operator Sign | S/N | *NAME OF MACHINE / EQUIPMENT | DAILY | Thur (Done / Not Done) | Engr / Operator Sign | Fri (Done / Not Done) | Engr / Operator Sign | Sat (Done / Not Done) | Engr / Operator Sign | Wk ...... (Done / Not Done) | Engr / Operator Sign
1 | STEAM BOILER 1 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve | [8 empty] | 1 | STEAM BOILER 1 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve
2 | STEAM BOILER 2 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve | [8 empty] | 2 | STEAM BOILER 2 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve
3 | STEAM BOILER 3 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve | [8 empty] | 3 | STEAM BOILER 3 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve
4 | THERMAX EXHAUST BOILER 4 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check proper operation of Boiler blowdown valve | [8 empty] | 4 | THERMAX EXHAUST BOILER 4 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check proper operation of Boiler blowdown valve
5 | STEAM BOILER 5 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve | [8 empty] | 5 | STEAM BOILER 5 | * Check for leakages (valves, mobrey, sight glass, manhole, etc) * Check proper operation of pumps (pump pressure, pump & motor overheating, etc.) * Check combustion chamber flame * Check proper operation of Boiler blowdown valve
6 | AIR COMPRESSOR NO.2 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 6 | AIR COMPRESSOR NO.2 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
7 | AIR COMPRESSOR NO.3 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 7 | AIR COMPRESSOR NO.3 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
8 | AIR COMPRESSOR NO.4 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 8 | AIR COMPRESSOR NO.4 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
9 | AIR COMPRESSOR NO.5 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 9 | AIR COMPRESSOR NO.5 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
10 | AIR COMPRESSOR NO.6 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 10 | AIR COMPRESSOR NO.6 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
11 | AIR COMPRESSOR NO.7 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 11 | AIR COMPRESSOR NO.7 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
12 | AIR COMPRESSOR NO.8 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 12 | AIR COMPRESSOR NO.8 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
13 | AIR COMPRESSOR NO.9 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 13 | AIR COMPRESSOR NO.9 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
14 | AIR COMPRESSOR NO.10 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 14 | AIR COMPRESSOR NO.10 (OIL-FREE). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
15 | AIR COMPRESSOR NO.11 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 15 | AIR COMPRESSOR NO.11 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
16 | AIR COMPRESSOR NO.12 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump | [8 empty] | 16 | AIR COMPRESSOR NO.12 (NORMAL). | * Check for oil and air leaks * Check for unusual noise on airend and electric motor * Check oil level in oil sump
17 | REFRIGERATED AIR DRYER NO.1 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 17 | REFRIGERATED AIR DRYER NO.1 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
18 | REFRIGERATED AIR DRYER NO.2 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 18 | REFRIGERATED AIR DRYER NO.2 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
19 | REFRIGERATED AIR DRYER NO.3 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 19 | REFRIGERATED AIR DRYER NO.3 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
20 | REFRIGERATED AIR DRYER NO.4 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 20 | REFRIGERATED AIR DRYER NO.4 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
21 | REFRIGERATED AIR DRYER NO.5 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 21 | REFRIGERATED AIR DRYER NO.5 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
22 | REFRIGERATED AIR DRYER NO.6 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 22 | REFRIGERATED AIR DRYER NO.6 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
23 | REFRIGERATED AIR DRYER NO.7 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 23 | REFRIGERATED AIR DRYER NO.7 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
24 | REFRIGERATED AIR DRYER NO.8 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 24 | REFRIGERATED AIR DRYER NO.8 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
25 | REFRIGERATED AIR DRYER NO.9 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 25 | REFRIGERATED AIR DRYER NO.9 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
26 | REFRIGERATED AIR DRYER NO.10 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve | [8 empty] | 26 | REFRIGERATED AIR DRYER NO.10 | * Check for air and refrigerant gas leaks * Check for unusual noise on compressor and HE blower fan * Check for proper operation of condensate drain valve
27 | TRANE CHILLER 1 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages | [8 empty] | 27 | TRANE CHILLER 1 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages
28 | TRANE CHILLER 2 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages | [8 empty] | 28 | TRANE CHILLER 2 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages
29 | TRANE CHILLER 3 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages | [8 empty] | 29 | TRANE CHILLER 3 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages
30 | TRANE CHILLER 4 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages | [8 empty] | 30 | TRANE CHILLER 4 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages
31 | TRANE CHILLER 5 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages | [8 empty] | 31 | TRANE CHILLER 5 | * Check log parameters on HMI * Check for oil and gas leaks * Check for proper operation of cond. and evap. line guages
32 | VAM CHILLER 1 | * Check for steam, condensate water leak on HTG * Check for air leak on steam control valve * Check for proper operation of guages | [8 empty] | 32 | VAM CHILLER 1 | * Check for steam, condensate water leak on HTG * Check for air leak on steam control valve * Check for proper operation of guages
33 | VAM CHILLER 2 | * Check for natural gas and diesel leaks on the line * Check for proper operation of guages | [8 empty] | 33 | VAM CHILLER 2 | * Check for natural gas and diesel leaks on the line * Check for proper operation of guages
34 | VAM CHILLER 3 | * Check for natural gas and diesel leaks on the line * Check for proper operation of guages | [8 empty] | 34 | VAM CHILLER 3 | * Check for natural gas and diesel leaks on the line * Check for proper operation of guages
35 | VAM CHILLER 4 | * Check for steam, condensate water leak on HTG * Check for air leak on steam control valve * Check for proper operation of guages | [8 empty] | 35 | VAM CHILLER 4 | * Check for steam, condensate water leak on HTG * Check for air leak on steam control valve * Check for proper operation of guages
36 | TRANE COOLING TOWER 1 | * Check for proper operation of water make-up float valve | [8 empty] | 36 | TRANE COOLING TOWER 1 | * Check for proper operation of water make-up float valve
37 | TRANE COOLING TOWER 2 | * Check for proper operation of water make-up float valve | [8 empty] | 37 | TRANE COOLING TOWER 2 | * Check for proper operation of water make-up float valve
38 | TRANE COOLING TOWER 3 | * Check for proper operation of water make-up float valve | [8 empty] | 38 | TRANE COOLING TOWER 3 | * Check for proper operation of water make-up float valve
39 | TRANE COOLING TOWER 4 | * Check for proper operation of water make-up float valve | [8 empty] | 39 | TRANE COOLING TOWER 4 | * Check for proper operation of water make-up float valve
40 | TRANE COOLING TOWER 5 | * Check for proper operation of water make-up float valve | [8 empty] | 40 | TRANE COOLING TOWER 5 | * Check for proper operation of water make-up float valve
41 | VAM COOLING TOWER 1 | * Check for proper operation of water make-up float valve | [8 empty] | 41 | VAM COOLING TOWER 1 | * Check for proper operation of water make-up float valve
42 | VAM COOLING TOWER 2 | * Check for proper operation of water make-up float valve | [8 empty] | 42 | VAM COOLING TOWER 2 | * Check for proper operation of water make-up float valve
43 | VAM COOLING TOWER 3 | * Check for proper operation of water make-up float valve | [8 empty] | 43 | VAM COOLING TOWER 3 | * Check for proper operation of water make-up float valve
44 | VAM COOLING TOWER 4 | * Check for proper operation of water make-up float valve | [8 empty] | 44 | VAM COOLING TOWER 4 | * Check for proper operation of water make-up float valve
45 | CARRIER CHILLER - AIR COOLED | * Check HP/LP pressure guages value | [8 empty] | 45 | CARRIER CHILLER - AIR COOLED | * Check HP/LP pressure guages value
46 | CLIVET CHILLER - AIR COOLED | * Check HP/LP pressure guages value | [8 empty] | 46 | CLIVET CHILLER - AIR COOLED | * Check HP/LP pressure guages value
47 | SOFTENER PLANT | * Check daily backwashing of softener plant * Check quantity of industrial salt in basin * Check for proper operation of auto controller | [8 empty] | 47 | SOFTENER PLANT | * Check daily backwashing of softener plant * Check quantity of industrial salt in basin * Check for proper operation of auto controller
48 | PRESSURE PRE-FILTER BAG TANK 25UM | * Check for leak on filter bag tank * Check differential pressure of filter bag tank inlet/outlet, if applicable | [8 empty] | 48 | PRESSURE PRE-FILTER BAG TANK 25UM | * Check for leak on filter bag tank * Check differential pressure of filter bag tank inlet/outlet, if applicable
49 | PRESSURE POST-FILTER BAG TANK 1UM | * Check for leak on filter bag tank * Check differential pressure of filter bag tank inlet/outlet, if applicable | [8 empty] | 49 | PRESSURE POST-FILTER BAG TANK 1UM | * Check for leak on filter bag tank * Check differential pressure of filter bag tank inlet/outlet, if applicable
50 | BOREHOLES | * Check for proper operation of pressure guages * Check for water leaks | [8 empty] | 50 | BOREHOLES | * Check for proper operation of pressure guages * Check for water leaks
51 | TREATED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.) | [8 empty] | 51 | TREATED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.)
52 | CHILLED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.) | [8 empty] | 52 | CHILLED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.)
53 | GENERAL | * Check for leaks on Treated Water, Boiler Feed, Chilled Water tanks * Check for proper operation of Treated Water, Boiler Feed, Chilled Water tanks level indicator and control valve * Drain condensate in Air Receiver tank | [8 empty] | 53 | GENERAL | * Check for leaks on Treated Water, Boiler Feed, Chilled Water tanks * Check for proper operation of Treated Water, Boiler Feed, Chilled Water tanks level indicator and control valve * Drain condensate in Air Receiver tank
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign |  | Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign
Note: N/A - Not Applicable | [10 empty] | Note: N/A - Not Applicable

## UTI PM Log - Weekly
| 4 Pages | 52 Copies
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI
[7 empty] | DEPARTMENT |  | ENGINEERING
[7 empty] | SECTION |  | UTILITY
[7 empty] | DOCUMENT NO |  | CHIENGUTRG08
ISSUE DATE
[7 empty] | PAGE NO |  | 1 OF 1
Legends
Done Ok "√", Not Done "--", Done Not Ok "X"
Date
S/N | *NAME OF MACHINE / EQUIPMENT | WEEKLY | Wk ...... (Done / Not Done) | Engr / Operator Sign | Wk …... (Done / Not Done) | Engr / Operator Sign | Wk …... (Done / Not Done) | Engr / Operator Sign | Wk …... (Done / Not Done) | Engr / Operator Sign
1 | STEAM BOILER 1 | * Physical inspection & lifting of safety relief valves * Physical inspection of mobrey float switch/motorized valve; check for proper operation
2 | STEAM BOILER 2 | * Physical inspection & lifting of safety relief valves * Physical inspection of mobrey float switch/motorized valve; check for proper operation
3 | STEAM BOILER 3 | * Physical inspection & lifting of safety relief valves * Physical inspection of mobrey float switch/motorized valve; check for proper operation
4 | THERMAX EXHAUST BOILER 4 | * Physical inspection of mobrey float switch; check for proper movement * Check proper operation of Boiler blowdown valve * Check electric motor current of running boiler pump
5 | STEAM BOILER 5 | * Physical inspection & lifting of safety relief valves * Physical inspection of mobrey float switch/motorized valve; check for proper operation
6 | AIR COMPRESSOR NO.2 (NORMAL). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
7 | AIR COMPRESSOR NO.3 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
8 | AIR COMPRESSOR NO.4 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
9 | AIR COMPRESSOR NO.5 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
10 | AIR COMPRESSOR NO.6 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
11 | AIR COMPRESSOR NO.7 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
12 | AIR COMPRESSOR NO.8 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
13 | AIR COMPRESSOR NO.9 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
14 | AIR COMPRESSOR NO.10 (OIL-FREE). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
15 | AIR COMPRESSOR NO.11 (NORMAL). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
16 | AIR COMPRESSOR NO.12 (NORMAL). | * Blowing of aftercooler HE and air filter * Check unload/load running current of electric motor and HE blower
17 | REFRIGERATED AIR DRYER NO.1 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
18 | REFRIGERATED AIR DRYER NO.2 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
19 | REFRIGERATED AIR DRYER NO.3 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
20 | REFRIGERATED AIR DRYER NO.4 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
21 | REFRIGERATED AIR DRYER NO.5 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
22 | REFRIGERATED AIR DRYER NO.6 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
23 | REFRIGERATED AIR DRYER NO.7 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
24 | REFRIGERATED AIR DRYER NO.8 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
25 | REFRIGERATED AIR DRYER NO.9 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
26 | REFRIGERATED AIR DRYER NO.10 | * Blowing of condenser HE and fan * Check level of water/glycol mixture, top up if required
27 | AIR RECEIVER TANKS | * Inspect air receiver tanks (leaks, pressure gauge, auto-drain) * Manually drain, if applicable
28 | VAM CHILLER 1 | * Check vacuum pump oil level
29 | VAM CHILLER 2 | * Check vacuum pump oil level
30 | VAM CHILLER 3 | * Check vacuum pump oil level
31 | VAM CHILLER 4 | * Check vacuum pump oil level
32 | TRANE COOLING TOWER 1 | * Check electric motor fan current
33 | TRANE COOLING TOWER 2 | * Check electric motor fan current
34 | TRANE COOLING TOWER 3 | * Check electric motor fan current
35 | TRANE COOLING TOWER 4 | * Check electric motor fan current
36 | TRANE COOLING TOWER 5 | * Check electric motor fan current
37 | VAM COOLING TOWER 1 | * Check electric motor fan current
38 | VAM COOLING TOWER 2 | * Check electric motor fan current
39 | VAM COOLING TOWER 3 | * Check electric motor fan current
40 | VAM COOLING TOWER 4 | * Check electric motor fan current
41 | SOFTENER PLANT | * Check for leakage of resin through bottom filter * Charging of industrial salt, if necessary * Check proper operation of unit
42 | PRESSURE PRE-FILTER BAG TANK 25UM | * Cleaning of filter bags
43 | PRESSURE POST-FILTER BAG TANK 1UM | * Cleaning of filter bags
44 | BH 1,4,5 DEGASSER | * Check for vibration on degasser blower base * Clean the air filters
45 | BH 2 DEGASSER | * Check for vibration on degasser blower base * Clean the air filters
46 | BH 6, 7 DEGASSER | * Check for vibration on degasser blower base * Clean the air filters
47 | PRESSURE GUAGES | * Check proper operation of guages
48 | TREATED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.)
49 | CHILLED WATER TRANSFER PUMPS | * Check proper operation of pumps (pump pressure, overheating, overcurrent, etc.)
50 | UTILITY DISTRIBUTION LINE | * Check for steam leak on steam distribution line * Check for air leak on air distribution line * Check for water leak on water distribution line * Check for chilled water leak on chilled water distribution line
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign
Note: N/A - Not Applicable

## UTI PM Log - Monthly
| 3 Pages | 12 Copies
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI
[7 empty] | DEPARTMENT |  | ENGINEERING
[7 empty] | SECTION |  | UTILITY
[7 empty] | DOCUMENT NO |  | CHIENGUTRG08
ISSUE DATE
[7 empty] | PAGE NO |  | 1 OF 1
Legends
Done Ok "√", Not Done "--", Done Not Ok "X"
Date
S/N | *NAME OF MACHINE / EQUIPMENT | MONTHLY | Month …... (Done / Not Done) | Engr / Operator Sign | Month …... (Done / Not Done) | Engr / Operator Sign | Month …... (Done / Not Done) | Engr / Operator Sign | Month …... (Done / Not Done) | Engr / Operator Sign
1 | STEAM BOILER 1 | * Check electric motor current of running boiler transfer pump, burner draft fan
2 | STEAM BOILER 2 | * Check electric motor current of running boiler transfer pump, burner draft fan
3 | STEAM BOILER 3 | * Check electric motor current of running boiler transfer pump, burner draft fan
4 | THERMAX EXHAUST BOILER 4 | * Check proper operation of blowdown valve
5 | STEAM BOILER 5 | * Check electric motor current of running boiler transfer pump, burner draft fan
6 | REFRIGERATED AIR DRYER NO.1 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
7 | REFRIGERATED AIR DRYER NO.2 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
8 | REFRIGERATED AIR DRYER NO.3 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
9 | REFRIGERATED AIR DRYER NO.4 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
10 | REFRIGERATED AIR DRYER NO.5 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
11 | REFRIGERATED AIR DRYER NO.6 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
12 | REFRIGERATED AIR DRYER NO.7 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
13 | REFRIGERATED AIR DRYER NO.8 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
14 | REFRIGERATED AIR DRYER NO.9 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
15 | REFRIGERATED AIR DRYER NO.10 | * Inspection of auto drain valves and filter * Check running current of compressor and HE blower fan
16 | CARRIER CHILLER - AIR COOLED | * Check oil level in compressor sump * Cleaning/washing of condenser
17 | CLIVET CHILLER - AIR COOLED | * Check oil level in compressor sump * Cleaning/washing of condenser
18 | VAM CHILLER 1 | * Cleaning of pump strainers
19 | VAM CHILLER 2 | * Cleaning of pump strainers
20 | VAM CHILLER 3 | * Cleaning of pump strainers
21 | VAM CHILLER 4 | * Cleaning of pump strainers
22 | TRANE COOLING TOWER 1 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
23 | TRANE COOLING TOWER 2 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
24 | TRANE COOLING TOWER 3 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
25 | TRANE COOLING TOWER 4 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
26 | TRANE COOLING TOWER 5 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
27 | VAM COOLING TOWER 1 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
28 | VAM COOLING TOWER 2 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
29 | VAM COOLING TOWER 3 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
30 | VAM COOLING TOWER 4 | * Draining and replenishment of treated water * Check proper operation of dosing pumps, foot valves, sensor * Inspection of extractor fan (U-bolts, coupling, locknuts, fan blades
31 | BOREHOLES | * Check for blockage on borehole water strainer and clean
32 | PRESSURE PRE-FILTER BAG TANK 25UM | * Inspect pressure filter bag tank gasket, replace if necessary * Replacement of pressure filter bags
33 | PRESSURE POST-FILTER BAG TANK 1UM | * Inspect pressure filter bag tank gasket, replace if necessary
34 | BH 1,4,5 DEGASSER | * Check the currect load on degasser blower
35 | BH 2 DEGASSER | * Check the currect load on degasser blower
36 | BH 6, 7 DEGASSER | * Check the currect load on degasser blower
37 | TREATED WATER TRANSFER PUMPS | * Lubrication of valves, Throttle manual valves (butterfly,klinger) continually until free * Check running current of electric motor
38 | CHILLED WATER TRANSFER PUMPS | * Lubrication of valves, Throttle manual valves (butterfly,klinger) continually until free * Check running current of electric motor
39 | PRESSURE GUAGES | * Check proper operation of guages
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign
Note: N/A - Not Applicable

## UTI PM Log - Quarterly
| 6 Pages | 4 Copies
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI
[7 empty] | DEPARTMENT |  | ENGINEERING
[7 empty] | SECTION |  | UTILITY
[7 empty] | DOCUMENT NO |  | CHIENGUTRG08
ISSUE DATE
[7 empty] | PAGE NO |  | 1 OF 1
Legends
Done Ok "√", Not Done "--", Done Not Ok "X"
Date
S/N | *NAME OF MACHINE / EQUIPMENT | QUARTERLY | Quarter …... (Done / Not Done) | Engr / Operator Sign | Quarter …... (Done / Not Done) | Engr / Operator Sign | Quarter …... (Done / Not Done) | Engr / Operator Sign | Quarter …... (Done / Not Done) | Engr / Operator Sign
1 | STEAM BOILER 1 | * Blowing of gas line filter * Open burner cover; inspect diesel and gas hose for damage, leak * Inspection & cleaning burner photocell * Cleaning of burner draft fan and sight glass
2 | STEAM BOILER 2 | * Blowing of gas line filter * Open burner cover; inspect diesel and gas hose for damage, leak * Inspection & cleaning burner photocell * Cleaning of burner draft fan and sight glass
3 | STEAM BOILER 3 | * Blowing of gas line filter * Open burner cover; inspect diesel and gas hose for damage, leak * Inspection & cleaning burner photocell * Cleaning of burner draft fan and sight glass
4 | STEAM BOILER 5 | * Blowing of gas line filter * Open burner cover; inspect diesel and gas hose for damage, leak * Inspection & cleaning burner photocell * Cleaning of burner draft fan and sight glass
5 | AIR COMPRESSOR NO.2 (NORMAL). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
6 | AIR COMPRESSOR NO.3 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
7 | AIR COMPRESSOR NO.4 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
8 | AIR COMPRESSOR NO.5 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
9 | AIR COMPRESSOR NO.6 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
10 | AIR COMPRESSOR NO.7 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
11 | AIR COMPRESSOR NO.8 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
12 | AIR COMPRESSOR NO.9 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
13 | AIR COMPRESSOR NO.10 (OIL-FREE). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
14 | AIR COMPRESSOR NO.11 (NORMAL). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
15 | AIR COMPRESSOR NO.12 (NORMAL). | * 2000 hours maintenance - hoses inspection and cleaning - pressure relief valve inspection & lifting, if applicable - check proper operation of thermostat
16 | REFRIGERATED AIR DRYER NO.1 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
17 | REFRIGERATED AIR DRYER NO.2 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
18 | REFRIGERATED AIR DRYER NO.3 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
19 | REFRIGERATED AIR DRYER NO.4 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
20 | REFRIGERATED AIR DRYER NO.5 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
21 | REFRIGERATED AIR DRYER NO.6 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
22 | REFRIGERATED AIR DRYER NO.7 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
23 | REFRIGERATED AIR DRYER NO.8 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
24 | REFRIGERATED AIR DRYER NO.9 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
25 | REFRIGERATED AIR DRYER NO.10 | * Inspection of condenser HE for damaged fins, blockage, etc * Inspection of blower fan for wear, damage, etc
26 | CARRIER CHILLER - AIR COOLED | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch etc.) * Inspect electrical components for deficiences * Check compressor crankcase heater functionality * Cleaning of pump strainers
27 | CLIVET CHILLER - AIR COOLED | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch etc.) * Inspect electrical components for deficiences * Check compressor crankcase heater functionality * Cleaning of pump strainers
28 | TRANE CHILLER 1 | * Routine inspection and checks by OEM/maintenance team * Cleaning of pump strainers * Poking of evaporator and condenser tubes
29 | TRANE CHILLER 2 | * Routine inspection and checks by OEM/maintenance team * Cleaning of pump strainers * Poking of evaporator and condenser tubes
30 | TRANE CHILLER 3 | * Routine inspection and checks by OEM/maintenance team * Cleaning of pump strainers * Poking of evaporator and condenser tubes
31 | TRANE CHILLER 4 | * Routine inspection and checks by OEM/maintenance team * Cleaning of pump strainers * Poking of evaporator and condenser tubes
32 | TRANE CHILLER 5 | * Routine inspection and checks by OEM/maintenance team * Cleaning of pump strainers * Poking of evaporator and condenser tubes
33 | VAM CHILLER 1 | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch, etc.) * Inspect electrical components for deficiences * Replacement of vacuum pump oil * LiBr analysis, corrosion inhibitor level
34 | VAM CHILLER 2 | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch, etc.) * Inspect electrical components for deficiences * Replacement of vacuum pump oil * LiBr analysis, corrosion inhibitor level
35 | VAM CHILLER 3 | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch, etc.) * Inspect electrical components for deficiences * Replacement of vacuum pump oil * LiBr analysis, corrosion inhibitor level
36 | VAM CHILLER 4 | * Preventive maintenance (leaks, component malfunction, sensor checks, flow switch, etc.) * Inspect electrical components for deficiences * Replacement of vacuum pump oil * LiBr analysis, corrosion inhibitor level
37 | TRANE COOLING TOWER 1 | * Cleaning of baffles * Cleaning of basin
38 | TRANE COOLING TOWER 2 | * Cleaning of baffles * Cleaning of basin
39 | TRANE COOLING TOWER 3 | * Cleaning of baffles * Cleaning of basin
40 | TRANE COOLING TOWER 4 | * Cleaning of baffles * Cleaning of basin
41 | TRANE COOLING TOWER 5 | * Cleaning of baffles * Cleaning of basin
42 | VAM COOLING TOWER 1 | * Cleaning of baffles * Cleaning of basin
43 | VAM COOLING TOWER 2 | * Cleaning of baffles * Cleaning of basin
44 | VAM COOLING TOWER 3 | * Cleaning of baffles * Cleaning of basin
45 | VAM COOLING TOWER 4 | * Cleaning of baffles * Cleaning of basin
46 | TREATED WATER TRANSFER PUMPS | * Cleaning of pump strainers
47 | CHILLED WATER TRANSFER PUMPS | * Cleaning of pump strainers
48 | BOILER FEED WATER TRANSFER PUMPS | * Cleaning of pump strainers
49 | PRESSURE POST-FILTER BAG TANK 1UM | * Replacement of filter bags
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign
Note: N/A - Not Applicable

## UTI PM Log - BiAnnually
| 4 Pages | 2 Copies
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT |  | CHI
[7 empty] | DEPARTMENT |  | ENGINEERING
[7 empty] | SECTION |  | UTILITY
[7 empty] | DOCUMENT NO |  | CHIENGUTRG08
ISSUE DATE
[7 empty] | PAGE NO |  | 1 OF 1
Legends
Done Ok "√", Not Done "--", Done Not Ok "X"
Date
S/N | *NAME OF MACHINE / EQUIPMENT | BIANNUALLY | Month 6 (Done / Not Done) | Engr / Operator Sign | Month 12 (Done / Not Done) | Engr / Operator Sign
1 | AIR COMPRESSOR NO.2 (NORMAL). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
2 | AIR COMPRESSOR NO.3 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element - check rubber insert of drive coupling, if applicable
3 | AIR COMPRESSOR NO.4 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element - check rubber insert of drive coupling, if applicable
4 | AIR COMPRESSOR NO.5 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
5 | AIR COMPRESSOR NO.6 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
6 | AIR COMPRESSOR NO.7 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
7 | AIR COMPRESSOR NO.8 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
8 | AIR COMPRESSOR NO.9 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
9 | AIR COMPRESSOR NO.10 (OIL-FREE). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
10 | AIR COMPRESSOR NO.11 (NORMAL). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
11 | AIR COMPRESSOR NO.12 (NORMAL). | * 4000 hours maintenance - air filter replacement - clean air condensate drain strainer - inspect condensate drain valves - clean breather element
12 | TRANE CHILLER 1 | * Cleaning of evaporator and condenser tubes
13 | TRANE CHILLER 2 | * Cleaning of evaporator and condenser tubes
14 | TRANE CHILLER 3 | * Cleaning of evaporator and condenser tubes
15 | TRANE CHILLER 4 | * Cleaning of evaporator and condenser tubes
16 | TRANE CHILLER 5 | * Cleaning of evaporator and condenser tubes
17 | VAM CHILLER 1 | * Cleaning of pump strainers * Inspect insulation of piping and corrosion on chiller parts * Clean liquid trap of purging line
18 | VAM CHILLER 2 | * Cleaning of pump strainers * Inspect insulation of piping and corrosion on chiller parts * Clean liquid trap of purging line
19 | VAM CHILLER 3 | * Cleaning of pump strainers * Inspect insulation of piping and corrosion on chiller parts * Clean liquid trap of purging line
20 | VAM CHILLER 4 | * Cleaning of pump strainers * Inspect insulation of piping and corrosion on chiller parts * Clean liquid trap of purging line
21 | STEAM TRAP | * Inspection of steam traps - proper discharge of condensate and check for blockage - steam leakage - proper functionality of isolation valves
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  | Status |  | Engr/ Operator Name & Sign |  | Manager Sign
Note: N/A - Not Applicable

## UTI PM Log - Annually
| 6 Pages | 1 Copy
CHI |  | UTILITY 1 PREVENTIVE MAINTENANCE LOG |  |  |  |  | BUSINESS UNIT | CHI
[7 empty] | DEPARTMENT | ENGINEERING
[7 empty] | SECTION | UTILITY
[7 empty] | DOCUMENT NO | CHIENGUTRG08
ISSUE DATE
[7 empty] | PAGE NO | 1 OF 1
Legends
Done Ok "√", Not Done "--", Done Not Ok "X"
|  | Date |  |  |  |  | Date
S/N | *NAME OF MACHINE / EQUIPMENT | ANNUALLY | (Done / Not Done) | Engr / Operator Sign | S/N | *NAME OF MACHINE / EQUIPMENT | ANNUALLY | (Done / Not Done) | Engr / Operator Sign
1 | STEAM BOILER 1 | * Annual overhauling of boiler * Burner fine-tuning and calibration * Cold & hot inspection of boiler * Servicing of gas train |  |  | 35 | VAM CHILLER 1 | * Annual overhaul of chillers * Cleaning of evaporator and condenser tubes
2 | STEAM BOILER 2 | * Annual overhauling of boiler * Burner fine-tuning and calibration * Cold & hot inspection of boiler * Servicing of gas train |  |  | 36 | VAM CHILLER 2 | * Annual overhaul of chillers * Cleaning of evaporator and condenser tubes
3 | STEAM BOILER 3 | * Annual overhauling of boiler * Burner fine-tuning and calibration * Cold & hot inspection of boiler * Servicing of gas train |  |  | 37 | VAM CHILLER 3 | * Annual overhaul of chillers * Cleaning of evaporator and condenser tubes
4 | THERMAX EXHAUST BOILER 4 | * Annual overhauling of boiler * Cold & hot inspection of boiler |  |  | 38 | VAM CHILLER 4 | * Annual overhaul of chillers * Cleaning of evaporator and condenser tubes
5 | STEAM BOILER 5 | * Annual overhauling of boiler * Burner fine-tuning and calibration * Cold & hot inspection of boiler * Servicing of gas train |  |  | 39 | TRANE COOLING TOWER 1 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
6 | AIR COMPRESSOR NO.2 (NORMAL). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 40 | TRANE COOLING TOWER 2 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
7 | AIR COMPRESSOR NO.3 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 41 | TRANE COOLING TOWER 3 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
8 | AIR COMPRESSOR NO.4 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 42 | TRANE COOLING TOWER 4 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
9 | AIR COMPRESSOR NO.5 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 43 | TRANE COOLING TOWER 5 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
10 | AIR COMPRESSOR NO.6 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 44 | VAM COOLING TOWER 1 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
11 | AIR COMPRESSOR NO.7 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 45 | VAM COOLING TOWER 2 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
12 | AIR COMPRESSOR NO.8 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 46 | VAM COOLING TOWER 3 | * Inspection of baffles and vents. Replace damaged ones * Thorough washing of baffles and vents
13 | AIR COMPRESSOR NO.9 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 47 | SOFTENER PLANT | * Inspection and replacment of resins, every 2 years
14 | AIR COMPRESSOR NO.10 (OIL-FREE). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 48 | MS TANKS | * Cleaning and disinfection of tank
15 | AIR COMPRESSOR NO.11 (NORMAL). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 49 | SS TANKS | * Cleaning and disinfection of tank
16 | AIR COMPRESSOR NO.12 (NORMAL). | * 8000 hours maintenance - air filter, oil filter, oil seperator & ultracoolant oil replacement - ultracoolant oil analysis - inspect starter contactors - clean seperator scavenge screen and orifice |  |  | 50 | TREATED WATER TRANSFER PUMPS | * Annual overhauling of transfer pumps
17 | REFRIGERATED AIR DRYER NO.1 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 51 | CHILLED WATER TRANSFER PUMPS | * Annual overhauling of transfer pumps
18 | REFRIGERATED AIR DRYER NO.2 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 52 | FLOWMETERS | * Annual calibration of flowmeters
19 | REFRIGERATED AIR DRYER NO.3 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 53 | PRESSURE GUAGES | * Annual calibration of pressure guages
20 | REFRIGERATED AIR DRYER NO.4 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 54 | AIR COMPRESSOR NO.2 (NORMAL). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
21 | REFRIGERATED AIR DRYER NO.5 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 55 | AIR COMPRESSOR NO.3 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
22 | REFRIGERATED AIR DRYER NO.6 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 56 | AIR COMPRESSOR NO.4 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
23 | REFRIGERATED AIR DRYER NO.7 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 57 | AIR COMPRESSOR NO.5 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
24 | REFRIGERATED AIR DRYER NO.8 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 58 | AIR COMPRESSOR NO.6 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
25 | REFRIGERATED AIR DRYER NO.9 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 59 | AIR COMPRESSOR NO.7 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
26 | REFRIGERATED AIR DRYER NO.10 | * Servicing of air dryer (sensor replacement), if required * Removal and pressure washing of condenser HE, if required * Service auto-drain valves |  |  | 60 | AIR COMPRESSOR NO.8 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
27 | TRANE CHILLER 1 | * Annual overhaul of chillers |  |  | 61 | AIR COMPRESSOR NO.9 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
28 | TRANE CHILLER 2 | * Annual overhaul of chillers |  |  | 62 | AIR COMPRESSOR NO.10 (OIL-FREE). | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
29 | TRANE CHILLER 3 | * Annual overhaul of chillers |  |  | 63 | AIR COMPRESSOR NO.11 (NORMAL) | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
30 | TRANE CHILLER 4 | * Annual overhaul of chillers |  |  | 64 | AIR COMPRESSOR NO.12 (NORMAL) | * 16000 hours maintenance - removal and pressure washing of aftercooler HE) - replace discharge check valve, if necessary - replace rubber insert of drive coupling, if necessary
31 | TRANE CHILLER 5 | * Annual overhaul of chillers |  |  | 65 | PRESSURE SAFETY RELIEF VALVES | * Annual inspection of pressure safety relief valves
32 | CARRIER CHILLER - AIR COOLED | * Oil analysis * Inspect insulation of piping and corrosion on chiller parts
33 | CLIVET CHILLER - AIR COOLED | * Oil analysis * Inspect insulation of piping and corrosion on chiller parts
34 | AIR RECEIVER TANKS | * Annual inspection of air receiver tanks (relief valves, UTM, etc.)
| Date | Gap Identified | Action Taken (Corrective/Preventive) |  |  |  | Status | Engr/ Operator Sign | Manager Sign
Note: N/A - Not Applicable

## Equipment PM (hidden)
BOILER & SOFTENER PLANT PREVENTIVE MAINTENANCE | Frequency | BOILER 1 |  | BOILER 2 |  | BOILER 5 |  | BOILER 3 |  | BOILER 4 |  | SOFTENER PLANT
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Charging of salt for backwashing | Weekly
* Replacement of resin beads every 2 years | 2-Years
* Physical inspection & lifting of safety relief valves | Weekly
* Check for leakages | Weekly
* Blowing of gas line filter | Monthly
* Inspection & cleaning burner photocell | Quarterly
* Cleaning of burner draft fan and sight glass | Quarterly
* Annual overhauling of boiler | Annually
* Burner fine-tuning and calibration | Annually
* Cold & hot inspection of boiler | Annually
* Servicing of gas train | Annually
AIR COMPRESSOR PREVENTIVE MAINTENANCE | Frequency | AIR COMPRESSOR NO. 2 |  | AIR COMPRESSOR NO. 3 |  | AIR COMPRESSOR NO. 4 |  | AIR COMPRESSOR NO. 5 |  | AIR COMPRESSOR NO. 6 |  | AIR COMPRESSOR NO. 7 |  | AIR COMPRESSOR NO. 8 |  | AIR COMPRESSOR NO. 9
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Blowing of intercooler, aftercooler and air filter | Weekly
* 2000 hours maintenance | 2000 hours
- hoses inspection and cleaning
- pressure relief valve inspection & lifting
* 4000 hours maintenance | 4000 hours
- air filter replacement
- clean condensate strainer/check autodrain valves
- check rubber insert of drive coupling
* 8000 hours maintenance | 8000 hours
- air filter, oil filter & ultracoolant oil replacement
- ultracoolant oil analysis
* 16000 hours maintenance | 16000 hours
- removal and pressure washing of condenser HE
- replace discharge check valve
- replace rubber insert of drive coupling, if necessary
AIR DRYER PREVENTIVE MAINTENANCE | Frequency | AIR DRYER NO. 5 |  | AIR DRYER NO. 6 |  | AIR DRYER NO. 7 |  | AIR DRYER NO. 8 |  | AIR DRYER NO. 9 |  | AIR DRYER NO. 10 |  | AIR DRYER NO. 11 |  | AIR DRYER NO. 1 |  | AIR DRYER NO. 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Blowing of condenser HE and fan | Weekly
* Check level of glycol, top up if required | Weekly
* Inspection of condenser | Quarterly
* Inspection of blower fan | Quarterly
* Inspection of auto drain valves | Quarterly
* Servicing of air dryer (sensor replacement) | Annually
* Removal and pressure washing of condenser HE | Annually
* Service auto-drain valves | Annually
TRANE CHILLER PREVENTIVE MAINTENANCE | Frequency | TRANE CHILLER 1 |  | TRANE CHILLER 2 |  | TRANE CHILLER 4 |  | TRANE CHILLER 5 |  | TRANE CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Monthly
* Preventive maintenance (leaks, component malfunction, sensor checks etc.) | Quarterly
* Inspect electrical components for deficiences | Quarterly
* Oil analysis | Annually
* Cleaning of evaporator and condenser tubes | Annually
* Inspect insulation of piping and corrosion on chiller parts | Annually
* Check crankcase heater functionality | Annually
* UT test on evaporator and condenser tubes every 2 years | Annually
VAM CHILLER PREVENTIVE MAINTENANCE | Frequency | VAM CHILLER 1 |  | VAM CHILLER 2 |  | VAM CHILLER 3 |  | VAM CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Monthly
* Blowing of gas filter | Monthly
* Annual overhaul of chiller | Annually
* Replacement of vacuum pump oil | Annually
* Cleaning of evaporator and condenser tubes | Annually
* Inspect insulation of piping and corrosion on chiller parts | Annually
* Servicing of gas train and burner fine-tuning/calibration | Annually
COOLING TOWER PREVENTIVE MAINTENANCE | Frequency | REHSLER COOLING TOWER 1 |  | REHSLER COOLING TOWER 2 |  | REHSLER COOLING TOWER 4 |  | REHSLER COOLING TOWER 5 |  | THERMAX COOLING TOWER 1 |  | THERMAX COOLING TOWER 2 |  | THERMAX COOLING TOWER 3 |  | REHSLER COOLING TOWER - UTILITY 2 |  | THERMAX COOLING TOWER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of cooling towers | Monthly
* Observe operation of float valve | Monthly
* Cleaning of pump strainers | Quarterly
* Annual overhaul and chemical cleaning of cooling towers | Annually
- Check to see that all bolts are tight in the fan and mechanical equipment region, including the fan guard
- Check structural bolted connections and tighten as required.
AIR RECEIVER TANK PREVENTIVE MAINTENANCE | Frequency | UTILITY WTP AIR RECEIVER TANK |  | UTILITY 1-5 K1 AIR RECEIVER 2 |  | WORKSHOP AIR RECEIVER TANK 1 & 2 |  | UHT 4 AIR RECEIVER TANK |  | SMB AIR RECEIVER TANK 3 |  | COMBI AIR RECEIVER TANK 4 |  | UHT 5 AIR RECEIVER TANK 7 |  | CAPRISONNE AIR RECEIVER TANK 8 & 9 |  | MITECO AIR RECEIVER TANK 1 & 2 |  | UTILITY 2 AIR RECEIVER TANK
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspect air receiver tanks (leaks, pressure gauge, auto-drain) | Monthly
* Annual inspection of air receiver tanks | Annually
UV DISINFECTANT PREVENTIVE MAINTENANCE | Frequency | UV DISINFECTANT 1 |  | UV DISINFECTANT 2 |  | UV DISINFECTANT 3 |  | UV DISINFECTANT 4
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspect UV glass tubes (electrical) | Monthly
* Cleaning of UV tube sleeves (electrical) | Quarterly
DEGASSER PREVENTIVE MAINTENANCE | Frequency | UTILITY 1 DEGASSER |  | BOREHOLE 2 DEGASSER |  | BOREHOLE 6 DEGASSER
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Physical inspection of degasser and blower (vibration, leaks, foundation bolts & nuts) | Weekly
* Check degasser blower motor bearing condition | Monthly
PRE-FILTER & POST-FILTER BAG / PRESSURE FILTER TANK PREVENTIVE MAINTENANCE | Frequency | PRE-FILTER BAG / PRESS. FILTER TANK 1 |  | PRE-FILTER BAG / PRESS. FILTER TANK 2 |  | PRE-FILTER BAG / PRESS. FILTER TANK 3 |  | PRE-FILTER BAG / PRESS. FILTER TANK 4 |  | PRE-FILTER BAG / PRESS. FILTER TANK 5 |  | PRE-FILTER BAG / PRESS. FILTER TANK 6 |  | POST-FILTER BAG 25UM
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of filter bags | Weekly
* Replacement of filter bags | Bi-annually
* Daily backwashing of filter tank | Daily
* Inspection of isolator, actuator valves, air hose | Monthly
* Inspection of blowers | Monthly
* Inspection of filter media and replenish where necessary | Annually
* Servicing of components (pressure switches, guages, air hose) | Annually
* Epoxy painting of vessels, if necessary | Annually
BOREHOLE PREVENTIVE MAINTENANCE | Frequency | BOREHOLE NO. 1 |  | BOREHOLE NO. 2 |  | BOREHOLE NO. 3 |  | BOREHOLE NO. 4 |  | BOREHOLE NO. 5 |  | BOREHOLE NO. 6 |  | BOREHOLE NO. 7
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspection of borehole for leakages, water pressure | Weekly
* Check current/amps of borehole electric motor (electrical) | Monthly
* Overhaul of borehole every 3 years | Weekly
DEGASSER PREVENTIVE MAINTENANCE | Frequency | UTILITY 1 DEGASSER |  | BOREHOLE 2 DEGASSER |  | BOREHOLE 6 DEGASSER
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Physical inspection of degasser and blower (vibration, leaks, foundation bolts & nuts) | Weekly
* Check degasser blower motor bearing condition | Monthly
STAND-ALONE EQUIPMENT PREVENTIVE MAINTENANCE | Frequency | RO PLANT |  | SS TANKS |  | GUERIN PD BLOWER |  | NEXGEN BLOWER |  | STEAM TRAP
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Backwashing of filter tanks | Weekly
* Cleaning of cartridge filter | Monthly
* Inspection of RO media | Annually
* Cleaning and disinfection of tanks | Annually
* Cleaning of blower air filter | Weekly
* Inspection of blower parts | Weekly
* Inspection of oil level, top up if necessary | Monthly
* Replace oil | Annually
* Replace air filter | Annually
* Replace oil filter | Annually
* Inspection of idler pulley and drive belt | Quarterly
* Blowing of air filter | Quarterly
* Replace drive belt | Annually
* Inspection of steam traps, replace if necessary | Bi-annually
NITROGEN GENERATOR PREVENTIVE MAINTENANCE | Frequency | NITROGEN GENERATOR 1 |  | VAM CHILLER 2 |  | VAM CHILLER 3 |  | VAM CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of filters | Quarterly
* Annual overhaul of nitrogen generator (filters) | Annually
* Replacement of sensors every 2 years | 2-Years
TRANSFER PUMPS PREVENTIVE MAINTENANCE | Frequency | CHILLED WATER TRANSFER PUMPS
|  | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Quarterly
* Check condition of bearings using CBM instrument | Quarterly
* Servicing of transfer pumps | Annually
MEASURING INSTRUMENTS PREVENTIVE MAINTENANCE | Frequency | pH METER |  | FLOWMETERS |  | PRESSURE GUAGES
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Calibration of pH meter | Monthly
* Annual calibration of flowmeters | Annually
* Annual calibration of pressure guages | Annually

## Equipment PM - Actual (hidden)
BOILER & SOFTENER PLANT PREVENTIVE MAINTENANCE | Frequency | BOILER 1 |  | BOILER 2 |  | BOILER 5 |  | BOILER 3 |  | BOILER 4 |  | SOFTENER PLANT
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Charging of salt for backwashing | Weekly
* Replacement of resin beads every 2 years | 2 Years
* Physical inspection & lifting of safety relief valves | Weekly
* Check for leakages | Weekly
* Blowing of gas line filter | Monthly
* Inspection & cleaning burner photocell | Quarterly
* Cleaning of burner draft fan and sight glass | Quarterly
* Annual overhauling of boiler | Annually
* Burner fine-tuning and calibration | Annually
* Cold & hot inspection of boiler | Annually
* Servicing of gas train | Annually
AIR COMPRESSOR PREVENTIVE MAINTENANCE | Frequency | AIR COMPRESSOR NO. 2 |  | AIR COMPRESSOR NO. 3 |  | AIR COMPRESSOR NO. 4 |  | AIR COMPRESSOR NO. 5 |  | AIR COMPRESSOR NO. 6 |  | AIR COMPRESSOR NO. 7 |  | AIR COMPRESSOR NO. 8 |  | AIR COMPRESSOR NO. 9
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Blowing of intercooler, aftercooler and air filter | Weekly
* 2000 hours maintenance | 2000 hours
- hoses inspection and cleaning
- pressure relief valve inspection & lifting
* 4000 hours maintenance | 4000 hours
- air filter replacement
- clean condensate strainer/check autodrain valves
- check rubber insert of drive coupling
* 8000 hours maintenance | 8000 hours
- air filter, oil filter & ultracoolant oil replacement
- ultracoolant oil analysis
* 16000 hours maintenance | 16000 hours
- removal and pressure washing of condenser HE
- replace discharge check valve
- replace rubber insert of drive coupling, if necessary
AIR DRYER PREVENTIVE MAINTENANCE | Frequency | AIR DRYER NO. 5 |  | AIR DRYER NO. 6 |  | AIR DRYER NO. 7 |  | AIR DRYER NO. 8 |  | AIR DRYER NO. 9 |  | AIR DRYER NO. 10 |  | AIR DRYER NO. 11 |  | AIR DRYER NO. 1 |  | AIR DRYER NO. 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Blowing of condenser HE and fan | Weekly
* Check level of glycol, top up if required | Weekly
* Inspection of condenser | Quarterly
* Inspection of blower fan | Quarterly
* Inspection of auto drain valves | Quarterly
* Servicing of air dryer (sensor replacement) | Annually
* Removal and pressure washing of condenser HE | Annually
* Service auto-drain valves | Annually
TRANE CHILLER PREVENTIVE MAINTENANCE | Frequency | TRANE CHILLER 1 |  | TRANE CHILLER 2 |  | TRANE CHILLER 4 |  | TRANE CHILLER 5 |  | TRANE CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Monthly
* Preventive maintenance (leaks, component malfunction, sensor checks etc.) | Quarterly
* Inspect electrical components for deficiences | Quarterly
* Oil analysis | Annually
* Cleaning of evaporator and condenser tubes | Annually
* Inspect insulation of piping and corrosion on chiller parts | Annually
* Check crankcase heater functionality | Annually
* UT test on evaporator and condenser tubes every 2 years | Annually
VAM CHILLER PREVENTIVE MAINTENANCE | Frequency | VAM CHILLER 1 |  | VAM CHILLER 2 |  | VAM CHILLER 3 |  | VAM CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Monthly
* Blowing of gas filter | Monthly
* Annual overhaul of chiller | Annually
* Replacement of vacuum pump oil | Annually
* Cleaning of evaporator and condenser tubes | Annually
* Inspect insulation of piping and corrosion on chiller parts | Annually
* Servicing of gas train and burner fine-tuning/calibration | Annually
COOLING TOWER PREVENTIVE MAINTENANCE | Frequency | REHSLER COOLING TOWER 1 |  | REHSLER COOLING TOWER 2 |  | REHSLER COOLING TOWER 4 |  | REHSLER COOLING TOWER 5 |  | THERMAX COOLING TOWER 1 |  | THERMAX COOLING TOWER 2 |  | THERMAX COOLING TOWER 3 |  | REHSLER COOLING TOWER - UTILITY 2 |  | THERMAX COOLING TOWER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of cooling towers | Monthly
* Observe operation of float valve | Monthly
* Cleaning of pump strainers | Quarterly
* Annual overhaul and chemical cleaning of cooling towers | Annually
- Check to see that all bolts are tight in the fan and mechanical equipment region, including the fan guard
- Check structural bolted connections and tighten as required.
AIR RECEIVER TANK PREVENTIVE MAINTENANCE | Frequency | UTILITY WTP AIR RECEIVER TANK |  | UTILITY 1-5 K1 AIR RECEIVER 2 |  | WORKSHOP AIR RECEIVER TANK 1 & 2 |  | UHT 4 AIR RECEIVER TANK |  | SMB AIR RECEIVER TANK 3 |  | COMBI AIR RECEIVER TANK 4 |  | UHT 5 AIR RECEIVER TANK 7 |  | CAPRISONNE AIR RECEIVER TANK 8 & 9 |  | MITECO AIR RECEIVER TANK 1 & 2 |  | UTILITY 2 AIR RECEIVER TANK
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspect air receiver tanks (leaks, pressure gauge, auto-drain) | Monthly
* Annual inspection of air receiver tanks | Annually
UV DISINFECTANT PREVENTIVE MAINTENANCE | Frequency | UV DISINFECTANT 1 |  | UV DISINFECTANT 2 |  | UV DISINFECTANT 3 |  | UV DISINFECTANT 4
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspect UV glass tubes (electrical) | Monthly
* Cleaning of UV tube sleeves (electrical) | Quarterly
DEGASSER PREVENTIVE MAINTENANCE | Frequency | UTILITY 1 DEGASSER |  | BOREHOLE 2 DEGASSER |  | BOREHOLE 6 DEGASSER
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Physical inspection of degasser and blower (vibration, leaks, foundation bolts & nuts) | Weekly
* Check degasser blower motor bearing condition | Monthly
PRE-FILTER & POST-FILTER BAG / PRESSURE FILTER TANK PREVENTIVE MAINTENANCE | Frequency | PRE-FILTER BAG / PRESS. FILTER TANK 1 |  | PRE-FILTER BAG / PRESS. FILTER TANK 2 |  | PRE-FILTER BAG / PRESS. FILTER TANK 3 |  | PRE-FILTER BAG / PRESS. FILTER TANK 4 |  | PRE-FILTER BAG / PRESS. FILTER TANK 5 |  | PRE-FILTER BAG / PRESS. FILTER TANK 6 |  | POST-FILTER BAG 25UM
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of filter bags | Weekly
* Replacement of filter bags | Bi-annually
* Daily backwashing of filter tank | Daily
* Inspection of isolator, actuator valves, air hose | Monthly
* Inspection of blowers | Monthly
* Inspection of filter media and replenish where necessary | Annually
* Servicing of components (pressure switches, guages, air hose) | Annually
* Epoxy painting of vessels, if necessary | Annually
BOREHOLE PREVENTIVE MAINTENANCE | Frequency | BOREHOLE NO. 1 |  | BOREHOLE NO. 2 |  | BOREHOLE NO. 3 |  | BOREHOLE NO. 4 |  | BOREHOLE NO. 5 |  | BOREHOLE NO. 6 |  | BOREHOLE NO. 7
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Inspection of borehole for leakages, water pressure | Weekly
* Check current/amps of borehole electric motor (electrical) | Monthly
* Overhaul of borehole every 3 years | Weekly
DEGASSER PREVENTIVE MAINTENANCE | Frequency | UTILITY 1 DEGASSER |  | BOREHOLE 2 DEGASSER |  | BOREHOLE 6 DEGASSER
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Physical inspection of degasser and blower (vibration, leaks, foundation bolts & nuts) | Weekly
* Check degasser blower motor bearing condition | Monthly
STAND-ALONE EQUIPMENT PREVENTIVE MAINTENANCE | Frequency | RO PLANT |  | SS TANKS |  | GUERIN PD BLOWER |  | NEXGEN BLOWER |  | STEAM TRAP
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Backwashing of filter tanks | Weekly
* Cleaning of cartridge filter | Monthly
* Inspection of RO media | Annually
* Cleaning and disinfection of tanks | Annually
* Cleaning of blower air filter | Weekly
* Inspection of blower parts | Weekly
* Inspection of oil level, top up if necessary | Monthly
* Replace oil | Annually
* Replace air filter | Annually
* Replace oil filter | Annually
* Inspection of idler pulley and drive belt | Quarterly
* Blowing of air filter | Quarterly
* Replace drive belt | Annually
* Inspection of steam traps, replace if necessary | Bi-annually
NITROGEN GENERATOR PREVENTIVE MAINTENANCE | Frequency | NITROGEN GENERATOR 1 |  | VAM CHILLER 2 |  | VAM CHILLER 3 |  | VAM CHILLER - UTILITY 2
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Cleaning of filters | Quarterly
* Annual overhaul of nitrogen generator (filters) | Annually
* Replacement of sensors every 2 years | 2-Years
TRANSFER PUMPS PREVENTIVE MAINTENANCE | Frequency | CHILLED WATER TRANSFER PUMPS
|  | LAST PM DATE | NEXT PM DATE
* Cleaning of pump strainers | Quarterly
* Check condition of bearings using CBM instrument | Quarterly
* Servicing of transfer pumps | Annually
MEASURING INSTRUMENTS PREVENTIVE MAINTENANCE | Frequency | pH METER |  | FLOWMETERS |  | PRESSURE GUAGES
|  | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE | LAST PM DATE | NEXT PM DATE
* Calibration of pH meter | Monthly
* Annual calibration of flowmeters | Annually
* Annual calibration of pressure guages | Annually