## Utility Equipment Standard (hidden)
UTILITY EQUIPMENT STANDARDS
Boiler | Value | Trane Chiller | Value | VAM Chiller | Value | Air Compressor IR | Value | Water Treatment | Value
Steam Pressure (bar) | 8.0 - 8.5 | Oil Pressure (kPa) | 1000 - 1200 | Chilled Water Temp. Differential (°C) | 5 - 8 °C | Oil Level | > 70% | Raw Water Tank 1 Level | > 20
Flame Signal (%) | > 90 | System Refrigerant Diff. Pressure (kPa) | 800 - 1000 | Chilled Water Inlet Pressure (bar) | > 0.8 bar | Package Disch. Pressure | 7.5 - 8.5 | Raw Water Tank 2 Level | > 90%
Conductivity (us/cm) | < 3500 | Comp Rfgt Discharge Temp (°C) | 63 - 66 | Chilled Water Outlet Pressure (bar) | > 0.4 bar | Package Disch. Temp. | 35 - 45 | Treated Water Tank Level | > 90%
Flue Gas Temperature (°C) | 130 - 250 | % RLA | < 95% | Hot/Cooling Water Flow rate |  | 1st Stage Inlet Temp. | 27 - 32 | Raw Water Pump Pressure | > 3.5 bar
Feed Water Tank Level | 90 - 95% | Evap Rfgt Sat. Temp. (°C) | > 1 | Hot/Cooling Water Inlet Temp. | 30 - 34 °C | 1st Stage Discharge Temp. | < 215 | Treated Water Pump Pressure | > 3.5 bar
Feed Water Tank Temperature | 85 - 95 °C | Evap Rfgt Pressure (kPa) | 300 - 400 | Hot/Cooling Water Outlet Temp. | 32 - 36 °C | 2nd Stage Inlet Pressure | 2.0 - 3.0 | Pre-Filter Bag Unit Inlet Pressure | > 1.1 bar
Feed Water pH | 8.0 - 10.0 | Evap Approach Temp (°C) | > 1 | Hot/Cooling Water Inlet Pressure | 2.3 - 2.5 bar | 2nd Stage Inlet Temp. | < 45 | Pre-Filter Bag Unit Outlet Pressure | > 0.8 bar
|  | Evap Rfgt Liquid Level (mm) | > 0 | Hot/Cooling Water Outlet Pressure | 1.3 - 1.5 bar | Bearing Oil Temp. | 55 - 65 | Post-Filter Bag Unit Inlet Pressure | > 4.0 bar
Boiler Water |  | Cond Rfgt Pressure (kPa) | 1100 - 1200 | High Temp. Generator Vapour Temp. |  | Bearing Oil Pressure | 1.8 - 2.0 | Post-Filter Bag Unit Outlet Pressure | > 3.8 bar
pH | 10.5 - 12.5 | Cond Inlet Temp. (°C) | 29 - 34 | U-tube Temp. |  | Oil Filter Pressure Drop | < 0.5 | Pressure Filter Tank Inlet Pressure | > 1.1
TDS | < 3500ppm | Cond Outlet Temp. (°C) | 35 - 39 | Low Temp. Generator |  | Inlet Vacuum | < 0.01 mmHg | Pressure Filter Tank Outlet Pressure | > 0.8
Conductivity (ppm) | < 7000ppm | Cond Sat Rfgt Temp (°C) | 42 - 48 | Spray Solution Temp. |  |  |  | Treated Water Outlet Pressure | 3.6 - 4.0 bar
Total Hardness (ppm) | 0 ppm | Condenser Approach Temp (°C) | 5.0 - 10.0 | High Temp. Generator Top Temp. |  |  |  | Water pH | 6.8 - 7.2
Phenolphthalein [P]-Alkalinity | 150 - 700 ppm |  |  | High Temp. Generator Bottom Temp. |  |  |  | UV Intensity | > 90 W/cm2
Total [M]-Alkalinity | < 1200ppm |  |  | Concentration | 60 - 63% |  |  | Backwashing Time
Caustic [O]-Alkalinity | 150 - 700 ppm |  |  | Vacuum Pressure mmHg | < 10mmHg
Sulphite | 20 - 40 ppm |  |  | Generator Fluid Level | > 70% | Air Dryer AC | Value | General Utility | Value
Phosphate | 10 - 30 ppm |  |  | Absorber Fluid Level | > 90% | Condensing Pressure | 25.5 bar | Outlet Temperature | 7 - 10 °C
|  |  |  | Evaporator Fluid Level | > 70% | Dryer LAT | 1.0 - 2.0 °C | Chilled Water Pump Pressure | 3.5 - 4.0 bar
|  |  |  | Steam Pressure before SCV |  | Refrigerant Temperature | 0 - 3 °C | Air Line Pressure | 6.8 - 8.0 bar
Air Compressor 2 | [5 empty] | Dryer Ambient Temperature | 28 - 30 °C | Steam Line Pressure | 7.5 - 8.5 bar
Aftercooler Discharge Temp. (°C) |  | Oil Pressure (kPa) |  |  |  | Refrigerant Compressor Outlet | 63 - 66 °C
Airend Discharge Temp. (°C) |  | System Refrigerant Diff. Pressure (kPa)
Injected Coolant Temp. (°C) |  | Comp Rfgt Discharge Temp (°C) |  |  |  | Air Dryer IR | Value
Separator Pressure Drop (bar) |  | % RLA |  |  |  | Air Inlet Temp. | 28 - 30 °C
Coolant Filter Pressure Drop (bar) | < 0.9 bar | Evap Entering Water Temp. (°C) |  |  |  | Dew Point | 1.0 - 2.0 °C
Coolant Filter |  | Evap Leaving Water Temp. (°C)
Inlet Vacuum (bar) |  | Evap Sat Rfgt Temp. (°C) | [5 empty] | Raw Water Tank 1 - 100,000 litres | > 90% |  | Oil Pressure (kPa) | 1000 - 1200
Inlet Vacuum (bar) |  | Evap Rfgt Pressure (kPa) |  | Air Dryer - Ingersoll Rand |  |  |  | Raw Water Tank 2 - 200,000 litres | > 90% |  | System Refrigerant Diff. Pressure (kPa) | 800 - 1000
Oil Level | 1/2 to 3/4 | Evap Approach Temp (°C) |  | Dew Point Pb1 (°C) |  |  |  | Process Water Tank 1 - 50,000 litres | > 90% |  | Comp Rfgt Discharge Temp (°C) | 60 - 70
Condensate Drain |  | Expansion Valve Position (%) |  | Air Inlet Temperature Pb2 (°C) |  | Steam Pressure (bar) | 8.0 - 8.5 | Process Water Tank 2 - 200,000 litres | > 90% |  | % RLA | < 95%
Air Leakage |  | Evap Rfgt Liquid Level (mm) |  | Ambient Temperature Pb3 (°C) |  | Flame Signal (%) | 90 - 95 % | Backwashing Water Tank - 50,000 litres | > 90% |  | Evap Entering Water Temp. (°C) | > 1
Water Leakage |  | Cond Rfgt Pressure (kPa) |  | Suction Temperature Pb4 (°C) |  | Conductivity (us/cm) | < 3500 | Raw Water Pumps Pressure (bar) | < 6 bar |  | Evap Leaving Water Temp. (°C) | 300 - 400
Noise Level (dB) |  | Cond Entering Water Temp. (°C) |  |  |  | Water Level (%) | 60 - 75 | Treated Water Pumps Pressure (bar) | > 3.5 bar |  | Evap Sat Rfgt Temp. (°C) | > 1
Internal/ External Body Clean |  | Cond Leaving Water Temp. (°C) |  | Air Dryer - Atlas Copco |  | Flue Gas Temperature (°C) | 130 - 250 | Raw Water pH | > 6.0 |  | Evap Rfgt Pressure (kPa) | > 0
|  | Cond Sat Rfgt Temp (°C) |  | Condensing Pressure (bar) |  | Fuel Pump Pressure | 12 - 25 bar | Process Water pH | 6.8 - 7.2 |  | Evap Approach Temp (°C) | 1000 - 1300
|  | Condenser Approach Temp (°C) |  | Dryer LAT (°C) |  | Oil Temperature | 40 - 75 °C | On-line Water pH | 6.8 - 7.2 |  | Expansion Valve Position (%)
|  |  |  | Refrigerant Temperature (°C) |  | Oil Pump Working No 1/2 | Alternate | Caustic Dosing Rate (l/hr) |  |  | Evap Rfgt Liquid Level (mm)
Pkg Discharge Pressure (bar) |  |  |  | Dryer Ambient Temperature (°C) |  | Feedwater Pump Working No 1/2 | Alternate | PRE-FILTER BAG UNIT |  |  | Cond Rfgt Pressure (kPa) | 35 - 45
Pkg Discharge Temp. (°C) |  |  |  | Refrigerant Compressor Outlet (°C) |  | Panel A/C Working Condition | Working/ Not Working | POST-FILTER BAG UNIT |  |  | Cond Entering Water Temp. (°C) | 42 - 48
1st Stage Discharge Temp. (°C) | [5 empty] | Water Leakage | No Leak/ Leak | PRESSURE FILTER TANK |  |  | Cond Leaving Water Temp. (°C) | 5.0 - 10.0
2nd Stage Inlet Pressure (bar) | [5 empty] | Steam Leakage | No Leak/ Leak | UV Intensity |  |  | Cond Sat Rfgt Temp (°C) | OK/Not OK
2nd Stage Inlet Temp. (°C) | [5 empty] | Burner Flame Sight Glass | Clear/ Not Clear | Borehole Line Pressure (bar) |  |  | Condenser Approach Temp (°C) | < 0.1
2nd Stage Discharge Pressure (bar) | [5 empty] | Blowdown Valve | Working/ Not Working
2nd Stage Discharge Temp. (°C)
Bearing Oil Temp. (°C)
Bearing Oil Pressure (bar)
Oil Filter Pressure Drop (bar) | < 0.9 bar
Oil Level | 1/2 to 3/4
Condensate Drain
Air Leakage
Water Leakage
Noise Level (dB)
Internal/ External Body Clean
Pkg Discharge Pressure (bar)
Pkg Discharge Temp. (°C)
Inlet Vaccum (bar)
1st Stage Inlet Temp. (°C)
1st Stage Discharge Temp. (°C)
2nd Stage Inlet Pressure (bar)
2nd Stage Inlet Temp. (°C)
2nd Stage Discharge Pressure (bar)
2nd Stage Discharge Temp. (°C)
Bearing Oil Temp. (°C)
Bearing Oil Pressure (bar)
Oil Filter Pressure Drop (bar)
Package kW (kW)
Oil Level
Condensate Drain
Air Leakage
Water Leakage
Noise Level (dB)
Internal/ External Body Clean
Raw Water Tank 1 100,000 litres | Raw Water Tank 2 200,000 litres | Process Water Tank 1 50,000 litres | Process Water Tank 2 200,000 litres | Backwashing Water Tank 50,000 litres | Raw Water Pumps Pressure (bar) | Treated Water Pumps Pressure (bar) | Raw Water pH | Process Water pH | On-line Water pH | Caustic Dosing Rate (l/hr) | Parameters | PRE-FILTER BAG UNIT 1 | PRE-FILTER BAG UNIT 2 | PRE-FILTER BAG UNIT 3 | PRE-FILTER BAG UNIT 4 | POST-FILTER BAG UNIT

## General Utility - Hourly (hidden)
[5 empty] | DEPARTMENT |  | ENGINEERING
[5 empty] | REGISTER NO |  | CHINGRGUT01
DATE
MONTH
DATE |  | BOILER WATER |  | UTILITY
|  | Feed Water Tank Level | Feed Water Tank Temperature | Chilled Water Outlet Temp. | Air Line Pressure | Steam Line Pressure | Operator
Standard |  | 80 - 90 % | 85 - 95 °C | 6 - 10 (°C) | 6.8 - 8.0 bar | 7.5 - 8.5 bar
July 2022
2022-07-01 | Day High
Day Low
2022-07-02 | Day High
Day Low
2022-07-03 | Day High
Day Low
2022-07-04 | Day High
Day Low
2022-07-05 | Day High
Day Low
2022-07-06 | Day High
Day Low
2022-07-07 | Day High
Day Low
2022-07-08 | Day High
Day Low
2022-07-09 | Day High
Day Low
2022-07-10 | Day High
Day Low
2022-07-11 | Day High
Day Low
2022-07-12 | Day High
Day Low
2022-07-13 | Day High
Day Low
2022-07-14 | Day High
Day Low
2022-07-15 | Day High
Day Low
2022-07-16 | Day High
Day Low
2022-07-17 | Day High
Day Low
2022-07-18 | Day High
Day Low
2022-07-19 | Day High
Day Low
2022-07-20 | Day High
Day Low
2022-07-21 | Day High
Day Low
2022-07-22 | Day High
Day Low
2022-07-23 | Day High
Day Low
2022-07-24 | Day High
Day Low
2022-07-25 | Day High
Day Low
2022-07-26 | Day High
Day Low
2022-07-27 | Day High
Day Low
2022-07-28 | Day High
Day Low
2022-07-29 | Day High
Day Low
2022-07-30 | Day High
Day Low
2022-07-31 | Day High
Day Low
Remarks
In-charge
HOD

## General Utility - Shift & Daily (hidden)
|  |  | GENERAL UTILITY | [15 empty] | DEPARTMENT |  | ENGINEERING
[19 empty] | REGISTER NO |  | CHINGRGUT01
DATE
MONTH
DATE |  | CHILLED WATER
|  | Pump 1 Pressure | Pump 2 Pressure | Pump 3 Pressure | Pump 4 Pressure | Pump 5 Pressure | Pump 6 Pressure | Pump 7 Pressure | Pump 8 Pressure | Pump 9 Pressure | Pump 10 Pressure | Pump 11 Pressure | Pump 12 Pressure | Feed Water pH | Feed Water TDS (ppm) | Feed Water Conductivity (us/cm) | Feed Water Total Hardness (ppm) | Feed Water P-Alkalinity | Feed Water M-Alkalinity | Feed Water O-Alkalinity | Feed Water Sulphite | Feed Water TSS | Operator
Standard |  | 3.5 - 4.5 bar | [11 empty] | 8 - 10 | < 2000 | < 2000 | 0
2022-07-01 | Morning Shift
Night Shift
2022-07-02 | Morning Shift
Night Shift
2022-07-03 | Morning Shift
Night Shift
2022-07-04 | Morning Shift
Night Shift
2022-07-05 | Morning Shift
Night Shift
2022-07-06 | Morning Shift
Night Shift
2022-07-07 | Morning Shift
Night Shift
2022-07-08 | Morning Shift
Night Shift
2022-07-09 | Morning Shift
Night Shift
2022-07-10 | Morning Shift
Night Shift
2022-07-11 | Morning Shift
Night Shift
2022-07-12 | Morning Shift
Night Shift
2022-07-13 | Morning Shift
Night Shift
2022-07-14 | Morning Shift
Night Shift
2022-07-15 | Morning Shift
Night Shift
2022-07-16 | Morning Shift
Night Shift
2022-07-17 | Morning Shift
Night Shift
2022-07-18 | Morning Shift
Night Shift
2022-07-19 | Morning Shift
Night Shift
2022-07-20 | Morning Shift
Night Shift
2022-07-21 | Morning Shift
Night Shift
2022-07-22 | Morning Shift
Night Shift
2022-07-23 | Morning Shift
Night Shift
2022-07-24 | Morning Shift
Night Shift
2022-07-25 | Morning Shift
Night Shift
2022-07-26 | Morning Shift
Night Shift
2022-07-27 | Morning Shift
Night Shift
2022-07-28 | Morning Shift
Night Shift
2022-07-29 | Morning Shift
Night Shift
2022-07-30 | Morning Shift
Night Shift
2022-07-31 | Morning Shift
Night Shift
Remarks
In-charge
HOD

## General
DEPARTMENT | ENGINEERING |  | UTILITY GENERAL LOG REPORT
DOCUMENT NO | CHIENGUTRG11
MONTH
DATE
EQUIPMENT | BOILER |  | CHILLED WATER |  |  |  | COMPRESSED AIR |  | Water Analysis
Parameters | Feed Water Tank Level (%) | Feed Water Tank Temp. (°C) | Chilled Water Tank Level (%) | CHI Snacks-1 Chilled Water Pump Pressure (bar) | CHI Snacks-2 Chilled Water Pump Pressure (bar) | Pharma Chilled Water Pump Pressure (bar) | Compressed Air Line Pressure (bar) |  | Cooling Tower Feedwater pH | Cooling Tower Feedwater Conductivity (us/cm)
8:00 | [7 empty] | Morning Shift
11:00 | [8 empty] | Cooling Tower Water Total Hardness (ppm) | Boiler Feedwater pH
14:00
17:00 | [7 empty] | Morning Shift
20:00 | [8 empty] | Boiler Feedwater Conductivity (us/cm) | Boiler Feedwater Total Hardness (ppm)
23:00
26:00 | [7 empty] | Morning Shift
29:00
EQUIPMENT | BOILER |  |  | COOLING TOWER |  |  | WTP
Parameters | Oxygen Scavenger Tank Level (%) | Sludge Dispersant Tank Level (%) | Sludge & Corrosion Inhibitor Tank Level (%) | Oxidizing Biocide Tank Level (%) | Non-Oxidizing Biocide Tank Level (%) | VAM Cooling Tower Basin Level (%) | Softener Plant Tank
| 25%/50%/75% | 25%/50%/75% | 25%/50%/75% | 25%/50%/75% | 25%/50%/75% | 25%/50%/75% | Salt/ No Salt
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. | [8 empty] | Manager Sign-off

## 2Tons Boiler
DEPARTMENT | ENGINEERING |  | 2 TONS/HR BOILER LOG REPORT
DOCUMENT NO | CHIENGUTRG03
MONTH
DATE
Parameters | Steam Pressure (bar) | Boiler Water Level (%) | Flue Gas Temperature (°C) | Water Level (%) | Flue Gas Temperature (°C) | Feedwater Pump Pressure (bar) | Oil Pump Working No 1/2 | Feedwater Pump Working No 1/2
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
Parameters | Water Leakage | Steam Leakage | Burner Flame Sight Glass | Blowdown Valve | Gas Pressure (high) (bar) | Gas Pressure (low) (mbar)
| No Leak/ Leak | No Leak/ Leak | Clear/ Not Clear | Working/ Not Working
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. | [6 empty] | Manager Sign-off

## WH Boiler
DEPARTMENT | ENGINEERING |  | 3.5 TONS/HR WASTE HEAT BOILER LOG REPORT
DOCUMENT NO | CHIENGUTRG03
MONTH
DATE
Parameters | From Engine-1 Temperature (°C) | From Engine-2 Temperature (°C) | From Engine-3 Temperature (°C) | To Chimney-1 Temperature (°C) | To Chimney-2 Temperature (°C) | To Chimney-3 Temperature (°C) | Boiler Steam Pressure (bar) | Boiler Water Level (%) | Level Control Valve Opening (%) | Feedwater Pump Working No 1/2
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
Parameters | Water Leakage | Steam Leakage | Blowdown Valve | Boiler Water Level Extra Low Safety | Engine-1 Safety | Engine-2 Safety | Engine-3 Safety | Boiler Steam Pressure High Safety | Feedwater Level
| No Leak/ Leak | No Leak/ Leak | Working/ Not Working | Okay/Not Okay | Okay/Not Okay | Okay/Not Okay | Okay/Not Okay |  | High/Low/Low-Low
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. | [8 empty] | Manager Sign-off

## WTP
DEPARTMENT | ENGINEERING |  | WATER TREATMENT PLANT LOG REPORT
DOCUMENT NO | CHIENGUTRG06
MONTH
DATE
Parameters | Process Water Tank Level (%) | Process Water Pressure (bar) | Process Water Flow Rate (m3/hr) | Water Pump Frequency (Hz) | Water Leakage Check ?
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. |  |  |  | Manager Sign-off

## Air Compressor
DEPARTMENT | ENGINEERING |  | IR MH75 AIR COMPRESSOR LOG REPORT
DOCUMENT NO | CHIENGUTRG01
MONTH
DATE
Parameters | Discharge Pressure (bar) | Airend Oil Temp. (°C) | Oil Sump Pressure (bar) | Running Hours | Loaded Hours
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
Parameters | Oil Level | Condensate Drain | Air Leakage | Water Leakage | Oil Leakage | Internal/ External Body Clean
| 1/2 to 3/4 | Functional/ Not Functional | No Leak/ Leakage | No Leak/ Leakage | No Leak/ Leakage | Clean/ Not Clean
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. |  |  |  |  | Manager Sign-off

## Air Dryer
DEPARTMENT | ENGINEERING |  | IR TMS AIR DRYER LOG REPORT
DOCUMENT NO | CHIENGUTRG02
MONTH
DATE
Parameters | Dew Point (°C) | Air Outlet Pressure (bar) | Condenser Pressure HP (bar) | Evaporator Pressure LP (bar)
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
Parameters | Condensate Drain | Air Leakage | Water Leakage | Internal/ External Body Clean
| Functional/ Not Functional | No Leak/ Leakage | No Leak/ Leakage | Clean/ Not Clean
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. |  |  |  | Manager Sign-off

## Clivet Chiller
DEPARTMENT | ENGINEERING |  | CLIVET CHILLER LOG REPORT
DOCUMENT NO | CHIENGUTRG07
MONTH
DATE
Parameters | Chilled Water Inlet Temperature (°C) | Chilled Water Outlet Temperature (°C) | Chilled Water Inlet Pressure (bar) | Chilled Water Outlet Pressure (bar) | Compressor 1 Condenser Pressure HP (bar) | Compressor 1 Evaporator Pressure LP (bar) | Compressor 2 Condenser Pressure HP (bar) | Compressor 2 Evaporator Pressure LP (bar)
8:00
10:00
12:00
14:00
16:00
18:00
20:00
22:00
24:00
26:00
28:00
30:00
Parameters | Compressor 1 Oil Level | Compressor 2 Oil Level | Chilled Water Outlet Pressure (bar) | Cooling Water Inlet Pressure (bar) | Refrigerant Leakage | Water Leakage | Components Physical Damage | Chilled Water Pump Working No 1/2
| Low/Normal/High | Low/Normal/High |  |  | No Leak/ Leakage | No Leak/ Leakage | No Damage/ Damage
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. | [5 empty] | Manager Sign-off

## VAM Chiller
DEPARTMENT | ENGINEERING |  | VAM CHILLER LOG REPORT
DOCUMENT NO | CHIENGUTRG07
MONTH
DATE
Parameters | Steam Control Valve Opening (%) | Chilled Water Inlet Temperature (°C) | Chilled Water Outlet Temperature (°C) | Cooling Water Inlet Temperature (°C) | Cooling Water Outlet Temperature (°C) | High Temperature Generator (°C) | High Temp. Generator Vapour (°C) | U-Tube Temperature (°C) | Low Temperature Generator (°C) | Spray Solution Temperature (°C) | High Temp. Generator Top (°C) | High Temp. Generator Bottom (°C) | Spray Solution Concentration (%) | Vacuum (mmHg) | Instant TR Generated
8:00
10:00
12:00
14:00
16:00
18:00
20:00
22:00
24:00
26:00
28:00
30:00
Parameters | Running Hours | Vacuum Pump Oil Level | Chilled Water Inlet Pressure (bar) | Chilled Water Outlet Pressure (bar) | Cooling Water Inlet Pressure (bar) | Cooling Water Outlet Pressure (bar) | High Temperature Generator Level | Absorber Level | Refrigerant Level | Chilled Water Pump Working No 1/2 | Cooling Water Pump Working No 1/2 | Cooling Tower Fan Working
|  | Below/On/Above |  |  |  |  | Low/Normal/High | Low/Normal/High | Low/Normal/High |  |  | One/Both
Morning Shift
Night Shift
Operator Morning Shift Name & Sign-off
Operator Night Shift Name & Sign-off
Alarm Fault/ Breakdown History | 1. 2. 3. | [9 empty] | Manager Sign-off

## Nitrogen (hidden)
DEPARTMENT | ENGINEERING |  | NITROGEN GENERATOR LOG REPORT
DOCUMENT NO | CHIENGUTLOGNG01
MONTH
YEAR
DATE | NITROGEN GENERATOR 1 | [5 empty] | NITROGEN GENERATOR 2
| N2 Purity (%) | Air Inlet Pressure (bar) | Nitrogen Outlet Pressure (bar) | Operating Hours | Flow rate (m³/hr) | Total flow (m³) | N2 Purity (%) | Air Inlet Pressure (bar) | Nitrogen Outlet Pressure (bar) | Operating Hours | Flow rate (m³/hr) | Total flow (m³) | Operators Name
1st
2nd
3rd
4th
5th
6th
7th
8th
9th
10th
11th
12th
13th
14th
15th
16th
17th
18th
19th
20th
21st
22nd
23rd
24th
25th
26th
27th
28th
29th
30th
31st
Alarm Fault/ Breakdown History | 1. 2. 3. | [11 empty] | Managers Sign-off

## VAM Chiller_ (hidden)
|  |  | CHILLER LOGBOOK THERMAX (THDC2) | [18 empty] | DEPARTMENT |  | ENGINEERING
[22 empty] | REGISTER NO |  | CHIENGUT07
DATE
MONTH
| COMPRESSOR REPORT | [8 empty] | EVAPORATOR REPORT |  |  |  | CONDENSER REPORT
TIME | Chilled Water Flow rate | Chilled Water Inlet Temp. (°C) | Chilled Water Outlet Temp. (°C) | Chilled Water Inlet Pressure (bar) | Chilled Water Outlet Pressure (bar) | Hot/Cooling Water Flow rate | Hot/Cooling Water Inlet Temp. | Hot/Cooling Water Outlet Temp. | Hot/Cooling Water Inlet Pressure | Hot/Cooling Water Outlet Pressure | High Temp. Generator Vapour Temp. | U-tube Temp. | Low Temp. Generator | Spray Solution Temp. | High Temp. Generator Top Temp. | High Temp. Generator Bottom Temp. | Absolute Difference | %Steam Control Valve Opening | Concentration | Vacuum Pressure mmHg | Generator Fluid Level | Absorber Fluid Level | Evaporator Fluid Level | Steam Pressure before SCV | Operator
Standard
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
19:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
31:00
Remarks | [10 empty] | Refrigerant Sp. Gravity
In-charge |  |  | START | STOP | HOURS |  |  |  | JOBS CARRIED OUT |  | Blowdown
[6 empty] | LOAD HOURS |  |  |  |  | Vacuum Pump - Oil Pump
Brine test
HOD |  |  | TOTAL RUNNING HOURS |  |  | UNLOAD HOURS
Note | 1. Figures in the bracket indicate acceptable norms
2. The inventory of this register shall be maintained by Engineering department
3. Any amendment to the register shall always be in co-ordinator with HOD Quality Management System

## Air Dryer IR (hidden)
|  | AIR DRYER LOGBOOK |  |  |  | DEPARTMENT |  | ENGINEERING
[6 empty] | REGISTER NO |  | CHIENGRGUT02
DATE
MONTH
| GENERAL CHECKING |  |  |  | TEMPERATURE (°C)
TIME | Condensate Drain | Air Leakage | Water Leakage | Noise Level | Air Inlet Temp. | Air Outlet Temp. | Dew Point | Operator
Standard
8:00
9:00
10:00
11:00
12:00
13:00
14:00
15:00
16:00
17:00
18:00
19:00
20:00
21:00
22:00
23:00
24:00
25:00
26:00
27:00
28:00
29:00
30:00
31:00
Remarks
In-charge |  | START | STOP | HOURS |  | JOBS CARRIED OUT
HOD
Note