## PROCESS WATER
PROCESS WATER MICROBIOLOGICAL SAMPLING PLAN CHICQARG24
S/N | SAMPLE | SAMPLING POINT | TEST/PARAMETER | NO/VOLUME OF SAMPLES | TEST METHOD | MEDIA USED | FREQUENCY OF TEST | INCUBATION |  | SPECIFICATION | ALERT LIMIT | ACTION/CRITICAL LIMIT
[8 empty] | TEMPERATURE(OC) | DURATION (HRS)
| Source water | Bore Hole 1,2,3,4,5,6,7 | Sensory (Smell, taste and Appearance) pH, hardness Turbidity *Alkalinity and TDS | Approx. 1,000ml - out of the well - after treatment - from production | [5 empty] | Pure, no off-smell or off-taste, 4.5 to 5.5 6.8 to 7.2 6.5 to 7.2 *Max 0.3 NTU *20 – 200 mg/L Max 500 mg/L
1 |  |  | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast & Mould | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 36±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 35±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
2 | Raw water | Inlet into water treatment and water storage tank | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast & Mould | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 35±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
3 | Treated water | Water from utility | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast & Mould | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 35±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 35±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
4 | Treated water | Water from TTAD processing | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast and mold | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 120 | 24/48 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 35±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 25±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
5 | Treated water | Water from Expansion processing | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast and mold | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 25±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 35±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
6 | Treated water | Water from New building processing | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast and mold | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 36±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 25±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
7 | Treated water | Water from Old building processing | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | < 100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 36±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast and mold | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 36±20c | 44 | < 1 cfu/250 ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 25±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
8 | Treated water | Water from Combi processing | Total count | 100ml | SM-PR-685 | Plate Count Agar w/o glucose | Weekly | 35±20c | 24/48 | <100 cfu/ 100ml | < 70 cfu/ 100ml | >100cfu/ 1ml
|  |  | Coliforms | 100ml | SM-PR-681 SM-PR-660 | Chromocult Coliform Agar | Weekly | 35±20c | 24/48 | < 1 cfu/ 100ml | N/A | ≥ 1cfu/100ml
|  |  | Yeast and mold | 100ml | SM-PR-688 SM-PR-660 | Yeast Extarct Agar w/o glucose | Monthly | 25±20c | 120 | < 10 cfu per 100 mL | < 5 cfu per 100 mL | ≥10 cfu/ 100ml
|  |  | Pseudomonas aeruginosa | 250ml | SM-PR-686 | External Analysis | Annually | 36±20c | 44 | < 1 cfu/ 250ml | N/A | >1cfu/250ml
|  |  | E. coli | 100ml | SM-PR-681 | E.M.B Agar | if Total coliforms is present | 35±20c | 24/48 | < 1 cfu/100 ml | N/A | ≥ 1cfu/100ml
9 | Utilities | Boiler Feed Water | pH |  | AOAC | NA | Weekly | NA | NA | 8.5-9.5
|  |  | Dissolved Oxygen |  |  |  | Weekly |  |  | <0.007 ppm
|  |  | Hardness |  |  |  | Weekly |  |  | <5 ppm
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <500 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | <1000 μS/cm
|  |  | P-Alkalinity |  |  |  | Weekly
|  |  | M-Alkalinity |  |  |  | Weekly
|  |  | Silica |  |  |  | Weekly |  |  | <20 ppm
|  |  | Chlorides |  |  |  | Weekly
11 |  | Boiler Water | pH |  |  |  | Weekly |  |  | 10.5-12.0
|  |  | Hardness |  |  |  | Weekly |  |  | 0 ppm
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <3000-5000 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | <6000 μS/cm
|  |  | P-Alkalinity |  |  |  | Weekly
|  |  | M-Alkalinity |  |  |  | Weekly
|  |  | Phosphates |  |  |  | Weekly |  |  | 30-60 ppm
|  |  | Sulfites |  |  |  | Weekly |  |  | 20-40 ppm
|  |  | Silica |  |  |  | Weekly |  |  | <150 ppm
|  |  | Iron (Fe) |  |  |  | Weekly |  |  | <500 ppm
|  |  | Chlorides |  |  |  | Weekly
12 |  | Boiler Blowdown water | pH |  |  |  | Weekly |  |  | 10.5-12.0
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly
|  |  | Conductivity |  |  |  | Weekly
|  |  | Silica |  |  |  | Weekly
|  |  | Phosphates |  |  |  | Weekly
13 |  | Softened Water | pH |  |  |  | Weekly |  |  | 7.0-8.5
|  |  | Hardness |  |  |  | Weekly |  |  | 0 ppm
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <1000 ppm
13 |  | RO Permeate water | pH |  |  |  | Weekly |  |  | 5.0-7.0
|  |  | Hardness |  |  |  | Weekly |  |  | <1 ppm
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <50 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | <100 μS/cm
|  |  | P-Alkalinity |  |  |  | Weekly
|  |  | M-Alkalinity |  |  |  | Weekly
|  |  | Silica |  |  |  | Weekly |  |  | <1 ppm
|  |  | Chlorides |  |  |  | Weekly |  |  | <10 ppm
14 |  | RO reject water | pH |  |  |  | Weekly |  |  | 6.5-8.5
|  |  | Hardness |  |  |  | Weekly
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | 1500-4000 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | 2000-6000 μS/cm
|  |  | Silica |  |  |  | Weekly
|  |  | Langelier Saturation Index |  |  |  | Weekly
15 |  | Chilled water | pH |  |  |  | Weekly |  |  | 7.0-9.0
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <1000 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | <1500 μS/cm
|  |  | Total Alkalinity |  |  |  | Weekly |  |  | 50-300 ppm
|  |  | Chlorides |  |  |  | Weekly |  |  | <500 ppm
|  |  | Iron (Fe) |  |  |  | Weekly |  |  | <2 ppm
10 |  | Cooling tower water | pH |  |  |  | Weekly |  |  | 6.5-8.5
|  |  | Hardness |  |  |  | Weekly |  |  | 200-800 ppm
|  |  | Total Dissolved Solids (TDS) |  |  |  | Weekly |  |  | <3000 ppm
|  |  | Conductivity |  |  |  | Weekly |  |  | <5000 μS/cm
|  |  | Total Alkalinity |  |  |  | Weekly |  |  | 100-500 ppm
|  |  | Chlorides |  |  |  | Weekly |  |  | <1000 ppm
|  |  | Phosphates |  |  |  | Weekly |  |  | 5-20 ppm
|  |  | Sulfates |  |  |  | Weekly |  |  | <1000 ppm
|  |  | Silica |  |  |  | Weekly |  |  | <150 ppm
|  |  | Iron (Fe) |  |  |  | Weekly |  |  | <2 ppm
|  |  | Langelier Saturation Index |  |  |  | Weekly |  |  | -0.5 to +2.0
|  |  | Cycles of Concentration |  |  |  | Weekly |  |  | 3-7
16 |  | VAM Chiller Lithiu Bromide | LiBr Concentration |  |  |  | Quarterly |  |  | 55-65%
|  |  | pH |  |  |  | Quarterly |  |  | 10.5-12.0
|  |  | Total Dissolved Solids (TDS) |  |  |  | Quarterly
|  |  | Density |  |  |  | Quarterly |  |  | 1.55-1.70 g/cm³
|  |  | Specific Gravity |  |  |  | Quarterly |  |  | 1.55-1.70
|  |  | Iron (Fe) |  |  |  | Quarterly |  |  | <10 ppm
|  |  | Copper (Cu) |  |  |  | Quarterly
|  |  | Chlorides |  |  |  | Quarterly |  |  | <50 ppm
|  |  | Viscocity |  |  |  | Quarterly
|  |  | Corrosion inhibitor concentration (Molybdate) |  |  |  | Quarterly |  |  | 0.5-2.0%
17 |  | ETP (pre softener and post softener) | TDS (inorganic and Organic),pH, COD, BOD, Hardness | Approx. 1,000ml |  |  | Fortnightly